## 2pipe system
Technical data required |  | MFP-34TA |  |  | MFP-51TA |  |  | MFP-68TA |  |  | MFP-85TA |  |  | MFP-102TA |  |  | MFP-136TA |  |  | MFP-170TA |  |  | MFP-204TA |  |  | MFP-238TA
2 tubes system
SPEED | unit | MAX | MED | MIN | MAX | MED | MIN | MAX | MED | MIN | MAX | MED | MIN | MAX | MED | MIN | MAX | MED | MIN | MAX | MED | MIN | MAX | MED | MIN | MAX | MED | MIN
Cooling capacity | kW | 1674 | 1390 | 1080 | 2484 | 2063 | 1605 | 3384 | 2810 | 2200 | 4300 | 3600 | 2760 | 5030 | 4180 | 3260 | 6700 | 5560 | 4380 | 8560 | 7080 | 5540 | 10050 | 8420 | 6520 | 11860 | 9800 | 7652
Sensible cooling capacity | kW | 1260 | 1100 | 880 | 1890 | 1620 | 1310 | 2600 | 2200 | 1800 | 3250 | 2800 | 2264 | 3820 | 3294 | 2660 | 5080 | 4380 | 3540 | 6450 | 5600 | 4550 | 7650 | 6570 | 5320 | 9000 | 7760 | 6250
Heating capacity | kW | 2020 | 1600 | 1260 | 3040 | 2390 | 1890 | 3990 | 3150 | 2450 | 4860 | 3845 | 3020 | 6080 | 4800 | 3780 | 7890 | 6220 | 4890 | 9990 | 7850 | 6200 | 12150 | 9600 | 7500 | 13600 | 10750 | 8440
Air flow | m3/h | 340 | 260 | 170 | 510 | 390 | 260 | 680 | 510 | 340 | 850 | 640 | 430 | 1020 | 770 | 510 | 1360 | 1020 | 680 | 1700 | 1280 | 850 | 2040 | 1530 | 1020 | 2380 | 1790 | 1190
Water flow | m3/h | 0.29 |  |  | 0.42 |  |  | 0.58 |  |  | 0.74 |  |  | 0.87 |  |  | 1.15 |  |  | 1.47 |  |  | 1.72 |  |  | 2.03
Water pressure drops | kPa | 7 |  |  | 15 |  |  | 18 |  |  | 23 |  |  | 28 |  |  | 30 |  |  | 22 |  |  | 30 |  |  | 36
Sound pressure power | dB(A) | 37 |  |  | 39 |  |  | 41 |  |  | 43 |  |  | 45 |  |  | 46 |  |  | 48 |  |  | 50 |  |  | 51
Fan power input (12Pa) | W | 27 | 25 | 21 | 43 | 33 | 27 | 59 | 46 | 37 | 66 | 62 | 56 | 95 | 84 | 73 | 118 | 92 | 71 | 144 | 126 | 114 | 186 | 152 | 126 | 224 | 202 | 178
Fan power input (30Pa) | W | 44 | 36 | 32 | 57 | 57 | 53 | 71 | 57 | 48 | 87 | 75 | 65 | 105 | 93 | 81 | 139 | 112 | 94 | 173 | 146 | 125 | 206 | 169 | 136 | 258 | 248 | 214
Fan power input (50Pa) | W | 48 | 39 | 36 | 63 | 55 | 47 | 84 | 72 | 59 | 97 | 85 | 73 | 113 | 105 | 96 | 157 | 135 | 108 | 204 | 184 | 164 | 233 | 228 | 202 | 287 | 285 | 256
Additional information about FAN
Electrical motor capacitor | uF | 1.2 |  |  | 1.8 |  |  | 2 |  |  | 2.5 |  |  | 3.2 |  |  | 2 |  |  | 2.5 |  |  | 3.2 |  |  | 3.2
Type of fan | Type | Centrifugal fan
Model of fan |  | PG150*200 |  |  | PG150*150 |  |  | PG150*200 |  |  | PG150*200 |  |  | PG150*200 |  |  | PG150*150 |  |  | PG150*200 |  |  | PG150*200 |  |  | PG150*200
Manufacturer of fan |  | ZHEJIANG LANGDI GROUP CO.,Ltd.
Number of fans | N° | 1 |  |  | 2 |  |  | 2 |  |  | 2 |  |  | 2 |  |  | 4 |  |  | 4 |  |  | 4 |  |  | 4
Number of motors | N° | 1 |  |  | 1 |  |  | 1 |  |  | 1 |  |  | 1 |  |  | 2 |  |  | 2 |  |  | 2 |  |  | 2
Fan rotation speed | rpm | 720 | 630 | 530 | 800 | 700 | 600 | 820 | 710 | 580 | 890 | 770 | 640 | 970 | 850 | 680 | 870 | 750 | 620 | 920 | 800 | 650 | 1080 | 920 | 780 | 1160 | 970 | 820
Sign or number repoted on the speed clamp |  | 2（H) | 3(M) | 4(L) | 2（H) | 3(M) | 4(L) | 2（H) | 3(M) | 4(L) | 2（H) | 3(M) | 4(L) | 2（H) | 3(M) | 4(L) | 2（H) | 3(M) | 4(L) | 2（H) | 3(M) | 4(L) | 2（H) | 3(M) | 4(L) | 2（H) | 3(M) | 4(L)
Colour of the fan speed wire |  | red | Blue | Black | red | Blue | Black | red | Blue | Black | red | Blue | Black | red | Blue | Black | red | Blue | Black | red | Blue | Black | red | Blue | Black | red | Blue | Black
Additional information about FINNED COIL
Number of rows | N° | 3
Number of branchlines | N° | 3in 3out
Number of tubes | N° | 24
Tubes pitch for rows pitch | mm | 22
Fins thickness | mm | 0.105
Fins spacing | mm | 2.2
Fins type |  | Blue fins
Outside tube diameter | mm | φ9.52
Coil lenght | mm | 451 |  |  | 501 |  |  | 651 |  |  | 801 |  |  | 851 |  |  | 1201 |  |  | 1351 |  |  | 1501 |  |  | 1651
Water inlet (bottom or top) |  | bottom
REFERENCE CONDITIONS
Cooling nominal condition:
indoor air temperature:27℃/50% RU
water temperature: 7℃/12℃, at maximum speed
Heating nominal condit
indoor air temperature: 20℃/50% RU
water inlet temperature: 50℃, at maximum speed,
with the same water flow as in cooling.

## 4-pipe system
Technical data required |  | MFP-34TA4 |  |  | MFP-51TA4 |  |  | MFP-68TA4 |  |  | MFP-85TA4 |  |  | MFP-102TA4 |  |  | MFP-136TA4 |  |  | MFP-170TA4 |  |  | MFP-204TA4 |  |  | MFP-238TA4
4 tubes system
SPEED | unit | MAX | MED | MIN | MAX | MED | MIN | MAX | MED | MIN | MAX | MED | MIN | MAX | MED | MIN | MAX | MED | MIN | MAX | MED | MIN | MAX | MED | MIN | MAX | MED | MIN
Cooling capacity | kW | 1674 | 1390 | 1080 | 2484 | 2063 | 1605 | 3384 | 2810 | 2200 | 4300 | 3600 | 2760 | 5030 | 4180 | 3260 | 6700 | 5560 | 4380 | 8560 | 7080 | 5540 | 10050 | 8420 | 6520 | 11860 | 9800 | 7652
Sensible cooling capacity | kW | 1260 | 1100 | 880 | 1890 | 1620 | 1310 | 2600 | 2200 | 1800 | 3250 | 2800 | 2264 | 3820 | 3294 | 2660 | 5080 | 4380 | 3540 | 6450 | 5600 | 4550 | 7650 | 6570 | 5320 | 9000 | 7760 | 6250
Heating capacity | kW | 1700 | 1360 | 1100 | 2550 | 2040 | 1600 | 3500 | 2780 | 2200 | 4500 | 3500 | 2750 | 5150 | 4080 | 3250 | 7080 | 5500 | 4460 | 8600 | 6750 | 5450 | 10200 | 8100 | 6500 | 11500 | 9900 | 7800
Air flow | m3/h | 340 | 260 | 170 | 510 | 390 | 260 | 680 | 510 | 340 | 850 | 640 | 430 | 1020 | 770 | 510 | 1360 | 1020 | 680 | 1700 | 1280 | 850 | 2040 | 1530 | 1020 | 2380 | 1790 | 1190
Water flow | m3/h | 0.29 |  |  | 0.42 |  |  | 0.58 |  |  | 0.74 |  |  | 0.87 |  |  | 1.15 |  |  | 1.47 |  |  | 1.72 |  |  | 2.03
Water pressure drops(cooling) | kPa | 7 |  |  | 15 |  |  | 18 |  |  | 23 |  |  | 28 |  |  | 30 |  |  | 22 |  |  | 30 |  |  | 36
Water flow | m3/h | 0.15 |  |  | 0.22 |  |  | 0.3 |  |  | 0.39 |  |  | 0.44 |  |  | 0.61 |  |  | 0.74 |  |  | 0.87 |  |  | 0.99
Water pressure drops(heating) | kPa | 2.8 |  |  | 6 |  |  | 7.2 |  |  | 9.2 |  |  | 11.2 |  |  | 12 |  |  | 8.8 |  |  | 12 |  |  | 14.4
Sound pressure power | dB(A) | 37 |  |  | 39 |  |  | 41 |  |  | 43 |  |  | 45 |  |  | 46 |  |  | 48 |  |  | 50 |  |  | 51
Fan power input (12Pa) | W | 27 | 25 | 21 | 43 | 33 | 27 | 59 | 46 | 37 | 66 | 62 | 56 | 95 | 84 | 73 | 118 | 92 | 71 | 144 | 126 | 114 | 186 | 152 | 126 | 224 | 202 | 178
Fan power input (30Pa) | W | 44 | 36 | 32 | 57 | 57 | 53 | 71 | 57 | 48 | 87 | 75 | 65 | 105 | 93 | 81 | 139 | 112 | 94 | 173 | 146 | 125 | 206 | 169 | 136 | 258 | 248 | 214
Fan power input (50Pa) | W | 48 | 39 | 36 | 63 | 55 | 47 | 84 | 72 | 59 | 97 | 85 | 73 | 113 | 105 | 96 | 157 | 135 | 108 | 204 | 184 | 164 | 233 | 228 | 202 | 287 | 285 | 256
Additional information about FAN
Electrical motor capacitor | uF | 1.2 |  |  | 2 |  |  | 2.5 |  |  | 2.5 |  |  | 2.5 |  |  | 2.5 |  |  | 2.5 |  |  | 3.2 |  |  | 3.5
Type of fan | Type | Centrifugal fan
Model of fan |  | PG150*200 |  |  | PG150*150 |  |  | PG150*200 |  |  | PG150*200 |  |  | PG150*200 |  |  | PG150*150 |  |  | PG150*200 |  |  | PG150*200 |  |  | PG150*200
Manufacturer of fan |  | ZHEJIANG LANGDI GROUP CO.,Ltd.
Number of fans | N° | 1 |  |  | 2 |  |  | 2 |  |  | 2 |  |  | 2 |  |  | 4 |  |  | 4 |  |  | 4 |  |  | 4
Number of motors | N° | 1 |  |  | 1 |  |  | 1 |  |  | 1 |  |  | 1 |  |  | 2 |  |  | 2 |  |  | 2 |  |  | 2
Fan rotation speed | rpm | 865 | 755 | 630 | 940 | 820 | 700 | 990 | 860 | 700 | 1050 | 910 | 750 | 1150 | 1020 | 815 | 1060 | 9150 | 750 | 1090 | 950 | 780 | 1300 | 1150 | 950 | 1430 | 1200 | 1010
Sign or number repoted on the speed clamp |  | 2（H) | 3(M) | 4(L) | 2（H) | 3(M) | 4(L) | 2（H) | 3(M) | 4(L) | 2（H) | 3(M) | 4(L) | 2（H) | 3(M) | 4(L) | 2（H) | 3(M) | 4(L) | 2（H) | 3(M) | 4(L) | 2（H) | 3(M) | 4(L) | 2（H) | 3(M) | 4(L)
Colour of the fan speed wire |  | red | Blue | Black | red | Blue | Black | red | Blue | Black | red | Blue | Black | red | Blue | Black | red | Blue | Black | red | Blue | Black | red | Blue | Black | red | Blue | Black
Additional information about COOLING FINNED COIL
Number of rows | N° | 3
Number of branchlines (cooling) | N° | 3in 3out
Number of tubes | N° | 24
Tubes pitch for rows pitch |  | 22
Fins thickness | mm | 0.105
Fins spacing | mm | 2.2
Fins type |  | Blue fins
Outside tube diameter | mm | φ9.52
Coil lenght | mm | 451 |  |  | 501 |  |  | 651 |  |  | 801 |  |  | 851 |  |  | 1201 |  |  | 1351 |  |  | 1501 |  |  | 1651
Water inlet (bottom or top) |  | bottom
Additional information about HEATING FINNED COIL
Number of rows | N° | 1
Number of branchlines | N° | 2in 2out
Number of tubes | N° | 8
Tubes pitch for rows pitch |  | 22
Fins thickness | mm | 0.105
Fins spacing | mm | 2.2
Fins type |  | Blue fins
Outside tube diameter | mm | φ9.52
Coil lenght | mm | 436 |  |  | 486 |  |  | 636 |  |  | 786 |  |  | 836 |  |  | 1186 |  |  | 1336 |  |  | 1486 |  |  | 1636
Water inlet (bottom or top) |  | bottom
REFERENCE CONDITIONS
Cooling nominal condition:
indoor air temperature:27℃/50% RU
water temperature: 7℃/12℃, at maximum speed
Heating nominal condit
indoor air temperature: 20℃/50% RU
water inlet temperature: 70/60℃, at maximum speed,