## C4-2P
TAIZHOU MECO REFRIGERATION EQUIPMENT Co.,Ltd
Price and Performance of high static pressure duct type fan coil unit(HAW series,2 pipe system)
model | unit | MFP-136HA(W) | MFP-170HA(W) | MFP-204HA(W) | MFP-238HA(W) | MFP-272HA(W) | MFP-306HA(W) | MFP-340HA(W) | MFP-408HA(W)
High speed | m3/h | 1360 | 1700 | 2040 | 2380 | 2720 | 3060 | 3400 | 4080
Medium speed | m3/h | 1090 | 1360 | 1635 | 1900 | 2180 | 2450 | 2720 | 3260
Low speed | m3/h | 815 | 1020 | 1225 | 1430 | 1630 | 1830 | 2040 | 2450
Cooling capacity | High speed kW | 7.2 | 9 | 10.8 | 12.6 | 14.4 | 16.2 | 18 | 21.6
| Middel speed kW | 5.45 | 6.8 | 8.15 | 9.5 | 10.85 | 12.25 | 13.6 | 16.3
| Low speed kW | 4.2 | 5.25 | 6.3 | 7.35 | 8.4 | 9.45 | 10.5 | 12.6
Heating capacity | High speed kW | 10.8 | 13.5 | 16.2 | 18.9 | 21.6 | 24.3 | 27 | 32.4
| Middel speed kW | 8.2 | 10.25 | 12.3 | 14.35 | 16.4 | 18.45 | 20.5 | 24.6
| Low speed kW | 7 | 8.8 | 10.55 | 12.3 | 14.05 | 15.8 | 17.55 | 21.05
Water volume | m3/h | 1.23 | 1.54 | 1.85 | 2.16 | 2.46 | 2.77 | 3.08 | 3.7
Static pressure | Pa | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
Water pressure dropping | kPa | 25 | 28 | 30 | 35 | 36 | 42 | 43 | 50
fan | type | double inlet forward-curve centrifugal fan
| quantity | 1 | 2
Motor | type | 3 speed permanent split capacity motor
| quantity | 1
| power supply | 220V~ 50Hz 1Ph
| power input(w) | 380 | 420 | 450 | 520 | 550 | 880 | 900 | 1100
Coil | type | Copper tube coat aluminum fin
| working pressure | 1.6MPa
| faced area(m2) | 0.256 | 0.285 | 0.285 | 0.334 | 0.334 | 0.402 | 0.402 | 0.494
Pipe connection | water inlet | 3/4"
| water outlet | 3/4"
| water drainage | 3/4"
| dimension(mm) | 970*760*425 | 1050*760*425 | 1050*760*425 | 1190*760*425 | 1190*760*425 | 1380*760*425 | 1380*760*425 | 1640*760*425
| net weight(kg) | 47 | 49 | 50 | 54 | 55 | 60 | 61 | 80
testing condition:
2 PIPE SYSTEM
REFERENCE CONDITIONS
Cooling nominal condition:
indoor air temperature:27℃/19.5℃ DB/WB
water temperature: 7℃/12℃, at maximum speed
Heating nominal condit
indoor air temperature: 20℃/15℃ DB/WB
water inlet temperature: 60℃, at maximum speed,
with the same water flow as in cooling.
MECO,the expert of FAN COIL UNIT | [8 empty] | Taizhou MECO Refrigeration Equipment Co.,Ltd
www.china-meco.com | [7 empty] | 2016-12-01

## C4-4P
TAIZHOU MECO REFRIGERATION EQUIPMENT Co.,Ltd
Price and Performance of high static pressure duct type fan coil unit(HAW series,4 pipe system)
model | unit | MFP-136HA(W)4 | MFP-170HA(W)4 | MFP-204HA(W)4 | MFP-238HA(W)4 | MFP-272HA(W)4 | MFP-306HA(W)4 | MFP-340HA(W)4 | MFP-408HA(W)4
High speed | m3/h | 1360 | 1700 | 2040 | 2380 | 2720 | 3060 | 3400 | 4080
Medium speed | m3/h | 1090 | 1360 | 1635 | 1900 | 2180 | 2450 | 2720 | 3260
Low speed | m3/h | 815 | 1020 | 1225 | 1430 | 1630 | 1830 | 2040 | 2450
Cooling capacity | High speed kW | 7.2 | 9 | 10.8 | 12.6 | 14.4 | 16.2 | 18 | 21.6
| Middel speed kW | 5.45 | 6.8 | 8.15 | 9.5 | 10.85 | 12.25 | 13.6 | 16.3
| Low speed kW | 4.2 | 5.25 | 6.3 | 7.35 | 8.4 | 9.45 | 10.5 | 12.6
Heating capacity | High speed kW | 4.6 | 5.76 | 6.9 | 8.05 | 9.2 | 10.4 | 11.5 | 13.8
| Middel speed kW | 3.5 | 4.4 | 5.25 | 6.15 | 7 | 7.9 | 8.75 | 10.5
| Low speed kW | 3 | 3.75 | 4.5 | 5.25 | 6 | 6.75 | 7.5 | 9
Water volume( COOLING) | m3/h | 1.23 | 1.54 | 1.93 | 2.16 | 2.46 | 2.77 | 3.08 | 3.7
Water volume( HEAING) |  | 0.53 | 0.66 | 0.8 | 0.92 | 1.06 | 1.19 | 1.32 | 1.58
Static pressure | Pa | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Water pressure dropping COOLING | kPa | 25 | 28 | 30 | 35 | 36 | 42 | 43 | 50
Water pressure dropping HEATING | kPa | 12 | 12 | 14 | 17 | 18 | 21 | 22 | 27
fan | type | double inlet forward-curve centrifugal fan
| quantity | 1 | 2
Motor | type | 3 speed permanent split capacity motor
| quantity | 1
| power supply | 220V~ 50Hz 1Ph
| power input(w) | 380 | 420 | 450 | 520 | 550 | 880 | 900 | 1100
Coil | type | Copper tube coat aluminum fin
| working pressure | 1.6MPa
| faced area(m2) | 0.256 | 0.285 | 0.285 | 0.334 | 0.334 | 0.402 | 0.402 | 0.494
Pipe connection(COOLING/HEATING) | water inlet | 3/4"
| water outlet | 3/4"
| water drainage | 3/4"
| dimension(mm) | 970*760*425 | 1050*760*425 | 1050*760*425 | 1190*760*425 | 1190*760*425 | 1380*760*425 | 1380*760*425 | 1640*760*425
| net weight(kg) | 49 | 51 | 52 | 56 | 57 | 63 | 64 | 84
testing condition:
4 PIPE SYSTEM
REFERENCE CONDITIONS
Cooling nominal condition:
indoor air temperature:27℃/19.5℃ DB/WB
water temperature: 7℃/12℃, at maximum speed
Heating nominal condit
indoor air temperature: 20℃/15℃ DB/WB
water inlet temperature: 60℃/50℃, at maximum speed,
MECO,the expert of FAN COIL UNIT | [8 empty] | Taizhou MECO Refrigeration Equipment Co.,Ltd
www.china-meco.com | [7 empty] | 2016-12-01